## Overview
|  |  | 9370-FB Series Fieldbus Segment Calculator Tool | [5 empty] | Version 1.01
Segment OK: 0 errors, 0 warnings.
|  |  |  | Project Name |  | MTL Sample Project1
|  |  |  | Segment Name |  | Segment #001
Host Control System |  |  |  | Date | 2010-08-30 | Name
Type |  |  |  | Comments
12
Host Current | 0 |  |  | Segment Properties
|  |  |  | Default trunk cable type |  |  | 13
|  |  |  | Default spur cable type |  |  | 44
|  |  |  | Max ambient cable temperature |  |  | 25
Fieldbus Power Supply |  |  |  | Default field device current |  |  | 20
Type |  |  |  | Default spur length |  |  | 20
Voltage | 28 |  |  | Field device minimum voltage |  |  | 9.5
Current | 500 |  |  | Spur short circuit test |  |  |  | Barrier 2 Spur 6
|  |  |  | Total trunk and spur length |  |  | 440
Length | 200 | 13 |  | Total current |  |  | 297.4671
Fieldbus Barrier 1
Type
Voltage | 27.2115 |  | Load | Length | Resistance | Tag |  |  | Voltage
Current | 141.987 | Spur 1 | 20 | 20 | 44 | Fieldbus Barrier 1 spur 1 |  |  | 11.9821
|  | Spur 2 | 20 | 20 | 44 | Fieldbus Barrier 1 spur 2 |  |  | 11.9821
|  | Spur 3 | 20 | 20 | 44 | Fieldbus Barrier 1 spur 3 |  |  | 11.9821
|  | Spur 4 | 20 | 20 | 44 | Fieldbus Barrier 1 spur 4 |  |  | 11.9821
|  | Spur 5 | 20 | 20 | 44 | Fieldbus Barrier 1 spur 5 |  |  | 11.9821
|  | Spur 6 | 20 | 20 | 44 | Fieldbus Barrier 1 spur 6 |  |  | 11.9821
Length | 0 | 13
Fieldbus Barrier 2
Type
Voltage | 27.2115 |  | Load | Length | Resistance | Tag |  |  | Voltage
Current | 155.4802 | Spur 1 | 20 | 20 | 44 | Fieldbus Barrier 2 spur 1 |  |  | 11.9821
|  | Spur 2 | 20 | 20 | 44 | Fieldbus Barrier 2 spur 2 |  |  | 11.9821
|  | Spur 3 | 20 | 20 | 44 | Fieldbus Barrier 2 spur 3 |  |  | 11.9821
|  | Spur 4 | 20 | 20 | 44 | Fieldbus Barrier 2 spur 4 |  |  | 11.9821
|  | Spur 5 | 20 | 20 | 44 | Fieldbus Barrier 2 spur 5 |  |  | 11.9821
|  | Spur 6 | 20 | 20 | 44 | Fieldbus Barrier 2 spur 6 |  |  | 11.9821
Approved | [6 empty] | Date
Lines below here should be hidden
MaxLength | MaxSpurLength | MinHubVolts | Res Coeff
1900 | 120 | 16 | 1.0195
Note on I21: Maximum length is 1900m
Validate

## Errors
Segment OK: 0 errors, 0 warnings.

## Settings (hidden)
|  | Power Supplies |  |  |  | Hosts |  |  | Hubs |  |  | Cables |  |  | Trunk Lengths | Segment Lengths
Debug | 0 | Name | Volts | Current (ma) | Selected Index | Name | Current (ma) | Selected Index | Name | Max spurs | Indices | Name | Resistance | Indices
|  | Custom | 24 | 500 | 3 | Custom | 0 | 1 | None | 0 | 3 | Custom | 44 | 2
Short Circuit | S/C Index | F801 | 21.5 | 350 |  | Emerson DeltaV | 24 |  | 9371/4-FB (4-spur) | 4 | 3 | 2.5mm² - AWG 13 | 13 | 7
No | 2 | F802 | 28 | 500 |  | Honeywell Series C | 24 |  | 9371-FB (6-spur) | 6 |  | 2.1mm² - AWG 14 | 17
Yes |  | F101 | 21.5 | 500 |  | Yokogawa Centum VP | 0 |  | 9373/8-FB (8-spur) | 8 |  | 1.5mm² - AWG 15 | 24
|  | F102 | 27.9 | 500 |  | Yokogawa Stardom | 0 |  | 9373-FB (12-spur) | 12 |  | 1.3mm² - AWG 16 | 28
|  | FPS-Series | 25 | 350 |  | ABB System 800xA | 0 |  |  |  |  | 1.0mm² - AWG 17 | 36
[6 empty] | Invensys Infusion | 0 |  |  |  |  | 0.8mm² - AWG 18 | 44

## Calculations (hidden)
Lengths
Trunk1 | 200 | Hub1 | 120 | Trunks | 200
Trunk2 | 0 | Hub2 | 120 | Spurs | 240
|  |  |  | Total | 440
|  | Currents | Device Current
|  | Hub1 | 120
|  | Hub2 | 120

## ReleaseNotes (hidden)
Revision | Date | Comments
1.00 | 2010-08-10 | Initial release
1.01 | 2010-09-01 | 1. Add message describing warnings and errors to sheet and update this dynamically when any values are changed. 2. Handle non numeric values in cells. Version 1.00 did not handle text or "deleted values" 3. Add "Approved" and "Date" boxes to the bottom of the sheet. 4. Correct quiescent currents for 9373 barriers.