## Index Page
Selected
120
See Data Sheets for Variants
9121-IS Simplex FISCO IIC
9122-IS Simplex FISCO IIB
9111-NI Simplex FNICO IIC
9112-NI Simplex FNICO IIC
FPS Single/Dual segment
MTL5995 Single segment DINrail
MTL5053 IS Entity Isolator
Fieldbus Segment Calculator
Copyright
MTL Instruments
Front Sheet
For queries
please call Luton Technical Support Group on
+44 (0)1582 - 723633
For terms & conditions of use refer to the User Manual
Key Notes
Version 1.5.4 June 2009
Instrument Data
F801 8-segment 24V
F802 8-segment 30V
910x-21 Redundant FISCO IIC 8-segment 24V
910x-22 Redundant FISCO IIB

## Auxiliary_Data
27
9121-IS
Network Source
Rosemount
Pressure Tx
8 | Spur | Instrument | Instr. | Process | [6 empty] | 3051
WAY | No. | Model | mA | Loop Name |  | Block 1 Instrument Details
| 1 | Level | 15 | LT505A1 | l |  |  |  | 13
| 2 | level | 15 | LT205A | [6 empty] | 18 |  | SL3 101
| 3 | Flow meter | 15 | UT105A | [8 empty] | SL3 102
| 4 | pressure | 15 | PIT1053 | [8 empty] | SL3 103
| 5 | DCV6000 | 25 | YIZ205A3 | [8 empty] | SL3 104
| 6 | spare | 10 | Spare | [8 empty] | SL3 105
| 7 | spare | 10 | Spare | [8 empty] | SL3 106
| 8 | spare | 10 | Spare | [8 empty] | SL3 107
| 9 | [11 empty] | SL3 108
10
[6 empty] | Surge | Entity | Zone 0
4 | Spur | Instrument | Instr. | Process |  | Block 2 Instrument Details
WAY | No. | Model | mA | Loop Name |  | Surge | Entity | Zone 0
| 1 | Flow control | 25 | FCV105A | l |  |  |  | 30
| 2 | Temp Control | 25 | TCV105A
| 3 | Spare | 10 | [6 empty] | ABB |  | Dresser Ledeen
| 4 | Spare | 10 | [6 empty] | Emerson |  | EIM
| 5 | [8 empty] | Endress & Hauser |  | Flowserve
| 6 | [8 empty] | Honeywell |  | Fuji
| 7 | [8 empty] | Foxboro |  | Krohne
| 8 | [8 empty] | Samson |  | Metso
| 9 | [8 empty] | Smar |  | Pepperl & Fuchs
| 10 | [8 empty] | VEGA |  | Rotork
[10 empty] | Westlock |  | StoneL
[10 empty] | Yokogawa |  | Topworx
[10 empty] | Buerkert Werke |  | Yamatake
4 | Spur | Instrument | Instr. | Process
WAY | No. | Model | mA | Loop Name |  | Block 3 Instrument Details
| 1 | Pressure | 18 | PIT105A2 | l |  |  |  | 47
| 2 | Pressure | 18 | PIT105A1
| 3 | Switch | 10 | XY105A
| 4 | Spare | 10
5
6
7
8
9
10
[6 empty] | Surge | Entity | Zone 0
4 | Spur | Instrument | Instr. | Process |  | Block 4 Instrument Details
WAY | No. | Model | mA | Loop Name |  | Surge | Entity | Zone 0
| 1 |  |  |  | l |  |  |  | 64
2
3
4
5
6
7
8
9
10
Manufacturer
to Main Menu
to Segment Layout
Write Megablock 1
Write Megablock 2
Write Megablock 3
Write Megablock 4
Read Megablock 1
Read Megablock 2
Read Megablock 3
Read Megablock 4
Design Current
Device / Model Number/s
Surge
Surge
Surge
Surge
Surge
Entity
Zone 0
Surge
Entity
Zone 0
Surge
Entity
Zone 0
Surge
Entity
Zone 0
Auto-insert Current Drawn
Move to foot of page
Move to top of page
mA
Manufacturers
data
Select
Instrument
to Main Menu
to Segment Layout
PRINT DATA
1
2
3
4
Transfer Instrument
Data to Block 'n'

## Network
9121-IS
Network Source
Selected
Intrinsic
Safety
selected
Min. Segment Voltage
Type 'A' | 44 |  | 9
MAIN MENU
Add 2-way Megablock
Add 4-way Megablock
Add 8-way Megablock
Add 10-way Megablock
CLEAR all Megablocks
SpurGuard
SYSTEM Check
CLEAR Check
PRINT
Instrument Data
1
2
3
4
CLEAR IS/SG Level
Select Cable
Apply
List Inventory

## Inst_Data
1 | ABB | Pressure Tx | 600T EN | 10.5
2 | ABB | Pressure Tx | 2010TD/TA 2020TG/TA | 12
3 | ABB | Temperature Tx | TF02 / TF02-EX | 10.5
4 | ABB | Temperature Tx | TF202 / TF202-EX | 10.5
5 | ABB | Vortex/Swirl Flow Meter | FV4000 / FS4000 | 10
6 | ABB | Electromagnetic Flowmeter | FXE4000 | 13
7 | ABB | Process Analyser pH/ORP/pION | TB82PH | 15
8 | ABB | Process Analyser Conductivity | TB82EC/TE/TC | 15
9 | ABB | Valve Positioner | TZIDC-120 | 11.5
10 | ABB | _ | _ | _
11 | ABB | _ | _ | _
12 | ABB | _ | _ | _
13 | ABB | _ | _ | _
14 | ABB | _ | _ | _
15 | ABB | _ | _ | _
16 | ABB | _ | _ | _
17 | ABB | _ | _ | _
18 | ABB | _ | _ | _
19 | ABB | _ | _ | _
20 | ABB | _ | _ | _
21 | Fisher Controls | Digital Valve Controller | DVC5000f AO/PID | 26
22 | Fisher Controls | Digital Valve Controller | DVC5000f DO/DI | 26
23 | Fisher Controls | Digital Valve Controller | DVC5000f | 26
24 | Fisher Controls | Digital Valve Controller | DVC6000 | 17
25 | MicroMotion | Coriolis Flow Meter | 5300 | 17
26 | MicroMotion | Coriolis Flow Meter | 2000 MVD | 11.5
27 | Rosemount | Pressure Tx | 3051 | 18
28 | Rosemount | Temperature Tx | 3244MV | 18
29 | Rosemount | Temperature Tx | 848T | 22
30 | Rosemount | Magnetic Flow Meter | 8742C | 12
31 | Rosemount | Vortex Flow Meter | 8800 | 18.5
32 | Rosem't Analytical | Flue Gas Tx | 4081 | 22
33 | Rosem't Analytical | Conductivity Tx | 4081C/T | 22
34 | Rosem't Analytical | pH Tx | 4081 | 22
35 | Rosem't Analytical | pH Tx | 5081 | 18
36 | Rosem't Analytical | Oxygen Analyser | 5081A | 22
37 | Rosem't Analytical | Oxymeter | 5000 | 17
38 | Rosem't Analytical | Continuous Gas Analyser | 1000 BINOS | 17
39 | EI-O-Matic | On-Off Extended | 0990 ELQ | 14.5
40 | EI-O-Matic | Positioner Extended | 7360 ELQ | 14.5
41 | Emerson | _ | _ | _
42 | Emerson | _ | _ | _
43 | Emerson | _ | _ | _
44 | Emerson | _ | _ | _
45 | Emerson | _ | _ | _
46 | Emerson | _ | _ | _
47 | Emerson | _ | _ | _
48 | Emerson | _ | _ | _
49 | Emerson | _ | _ | _
50 | Emerson | _ | _ | _
51 | Emerson | _ | _ | _
52 | Emerson | _ | _ | _
53 | Emerson | _ | _ | _
54 | Emerson | _ | _ | _
55 | Emerson | _ | _ | _
56 | Emerson | _ | _ | _
57 | Emerson | _ | _ | _
58 | Emerson | _ | _ | _
59 | Emerson | _ | _ | _
60 | Emerson | _ | _ | _
61 | Endress & Hauser | Pressure Tx | Cerebar S | 11
62 | Endress & Hauser | Pressure Tx | Deltabar S PMP230/235 | 11
63 | Endress & Hauser | Level Tx | Deltapilot S | 11
64 | Endress & Hauser | Level Tx | Micropilot II | 13
65 | Endress & Hauser | Level Tx | Micropilot M | 15
66 | Endress & Hauser | Electromagnetic Flowmeter | Promag53 | 12
67 | Endress & Hauser | Ultrasonic Flowmeter | Prosonic93 | 12
68 | Endress & Hauser | Temperature Tx | TMT 165 | 12
69 | Endress & Hauser | Coriolisss Flow Meter | Promass83 | 12
70 | Endress & Hauser | Radar Level Tx | Levelflex M | 15
71 | Endress & Hauser | Ultrasonic Level Tx | Prosonic M | 12
72 | Endress & Hauser | _ | _ | _
73 | Endress & Hauser | _ | _ | _
74 | Endress & Hauser | _ | _ | _
75 | Endress & Hauser | _ | _ | _
76 | Endress & Hauser | _ | _ | _
77 | Endress & Hauser | _ | _ | _
78 | Endress & Hauser | _ | _ | _
79 | Endress & Hauser | _ | _ | _
80 | Honeywell | Pressure Tx | ST3000FF | 20
81 | Honeywell | Temperature Tx | STT35F | 18
82 | Honeywell | _ | _ | _
83 | Honeywell | _ | _ | _
84 | Foxboro | Digital Positioner | SRD991 | 11
85 | Foxboro | Digital Positioner | SRD960 | 11
86 | Foxboro | _ | _ | _
87 | Foxboro | _ | _ | _
88 | Samson | Valve Positioner | 3787 | 15
89 | Samson | _ | _ | _
90 | Samson | _ | _ | _
91 | Smar | Current Output Tx | FI302 | 12
92 | Smar | Current Tx | IF302 | 12
93 | Smar | Pressure Tx | LD302 | 12
94 | Smar | Temperature Tx | TT302 | 12
95 | Smar | Advanced Positioner Tx | FP302 | 12
96 | Smar | Basic Positioner Tx | FY302 | 12
97 | Smar | _ | _ | _
98 | Smar | _ | _ | _
99 | Smar | _ | _ | _
100 | Smar | _ | _ | _
101 | VEGA | Radar level measurement | VEGAPULS 60 | 10
102 | VEGA | Guided microwave level measurement | VEGAFLEX 60 | 10
103 | VEGA | Ultrasonic level measurement | VEGASON 60 | 10
104 | VEGA | Pressure measurement | VEGABAR 50/60 | 10
105 | VEGA | _ | _ | _
106 | VEGA | _ | _ | _
107 | VEGA | _ | _ | _
108 | Westlock | Valve Controller | EL40106 | 16
109 | Westlock | _ | _ | _
110 | Westlock | _ | _ | _
111 | Yokogawa | Pressure Tx | EJA Series | 16.5
112 | Yokogawa | Vortex Flow Meter | YEWFLO DY/DYA Series | 11
113 | Yokogawa | Temperature Tx | YTA320 | 16.5
114 | Yokogawa | Valve Positioner | YVP110 | 17
115 | Yokogawa | Magnetic Flow Meter | ADMAG AE | 17
116 | Yokogawa | Chart Recorder | DAQSTATION | 16.5
117 | Yokogawa | Inductance/Conductivity Meter | SC202-F | 22
118 | Yokogawa | pH/ORP Meter | PH202-F | 22
119 | Yokogawa | Conductivity/Resistivity Meter | ISC202-F | 22
120 | Yokogawa | _ | _ | _
121 | Yokogawa | _ | _ | _
122 | Yokogawa | _ | _ | _
123 | Yokogawa | _ | _ | _
124 | Yokogawa | _ | _ | _
125 | Buerkert Werke | Power I/O Box | 8643 | 30
126 | Buerkert Werke | _ | _ | _
127 | Buerkert Werke | _ | _ | _
128 | Dresser Ledeen | Flow Control | FVP110 | 17.5
129 | Dresser Ledeen | _ | _ | _
130 | Dresser Ledeen | _ | _ | _
131 | EIM | Valve Positioner | EA00 | 17.5
132 | EIM | On-Off Valve | ED00 | 17.5
133 | EIM | _ | _ | _
134 | EIM | _ | _ | _
135 | EIM | _ | _ | _
136 | EIM | _ | _ | _
137 | Flowserve | Valve Controller | Logix1400 | 23
138 | Flowserve | _ | _ | _
139 | Flowserve | _ | _ | _
140 | Fuji | Pressure Tx | FCX-A2 | 20
141 | Fuji | _ | _ | _
142 | Fuji | _ | _ | _
143 | Krohne | Radar Level Tx | BM70A | 16
144 | Krohne | _ | _ | _
145 | Krohne | _ | _ | _
146 | Metso | Valve Positioner | ND830 / ND800 FF | 23
147 | Metso | Valve Positioner | ND9000F | 17
148 | Metso | _ | _ | _
149 | Metso | _ | _ | _
150 | Pepperl & Fuchs | Valve Positioner Interface | FDO-VC-Ex4.FF | 23
151 | Pepperl & Fuchs | _ | _ | _
152 | Pepperl & Fuchs | _ | _ | _
153 | Rotork | Valve Actuator |  | 20
154 | Rotork | _ | _ | _
155 | Rotork | _ | _ | _
156 | StoneL | Valve Actuator | FF VCT | 20
157 | StoneL | _ | _ | _
158 | StoneL | _ | _ | _
159 | Topworx | Valve Controller | DVC-FF | 23
160 | Topworx | _ | _ | _
161 | Topworx | _ | _ | _
162 | Yamatake | Magnetic Flow Meter | MagneW 3000 | 12
163 | Yamatake | Temperature Tx | ATT60 | 20
164
165
166
167
168
169
170

## Key Notes
to Main Menu
to Segment Layout
Selection of SpurGuard Option
Please remember to select or de-select the SpurGuard option before placing the Megablock device/s on the Network layout. All subsequent selections then define that type of device.
If the option is not as required, and a megablock is placed down, it can only be changed by deleting the megablock completely and making a new selection.
Intrinsic Safety Option
The Intrinsic Safety option is automatically selected based on the selected power supply. If your power supply is Entity, FISCO or redundant FISCO type, your Megablocks are required to be intrinsically safe. For all non-IS power supplies, Megablocks are to be non-intrinsically safe type.
User Minimum Network Voltage
Ensure this user-selected minimum network voltage is set to your requirement on the 'Network Sheet' prior to system design commencing. The default value, following the Fieldbus specification, is 9.0 volts. Some users may wish to increase this value for contingency, for example to 9.5 volts.

## Front Sheet
Documentation Header
Customer:
Address
Engineer:
Supervisor
Date:
Engineer:
Project Version | Vers. 1.0.15
Date : | 21 May 2008
This information may be printed out
with the network design details
to Main Menu
to Segment Layout
PRINT Full Project Design